CLOSED SYSTEM TREATMENT LOOP N-93

# FOR CLOSED HEATING OR COOLING SYSTEMS

ChemREADY’s Closed System Treatment LOOP N-93 is a liquid no-color-added blend of inorganic nitrite, and borate combined with organic copper corrosion inhibitors and scale control agents. Green color can be added upon request.

# USES

Closed System Treatment LOOP N-93 is used to provide complete protection to closed water systems containing a variety of dissimilar metals. When used at the recommended dosage, formula LOOP N-93 will keep systems free from damaging corrosion. Closed System Treatment LOOP N-93 is compatible with glycol systems.

# PRODUCT DESCRIPTION

Physical State - Liquid

Color – Light Yellow Liquid  Density - 10.4 lbs./gallon  pH - 12.0

# DISSIMILAR METALS/ ELECTROLYSIS

TECHNICAL   BULLETIN

Various metals in contact with each other in an aqueous environment will exhibit electrolysis, the corrosion of the least noble metal. Corrosion Inhibitors such as formula LOOP N-93 will minimize this chemical activity.

# DOSAGE

Closed System Treatment LOOP N-93 should be used at 5 gallon per 1000 gallon system capacity. Use the softest water available in the system. The system should be monitored periodically using a nitrite test kit. Nitrite concentrations should be between 800 and 1,000 ppm. For additional information on product application, contact your Ques Industries representative.

# HANDLING

System Treatment LOOP N-93 is an alkaline material. Do not take internally. Avoid contact with skin and eyes. Should contact occur, flush immediately with water. If any discomfort persists, seek medical attention. Read relevant Safety Data Sheet before handling this product.

# PACKAGING

Closed System Treatment LOOP N-93 is packaged in 55, 30 and 15 gallon non-returnable drums, 5 gallon pails and 275 gallon totes.

3/22

"Technical data is afforded solely for your evaluation, independently of the sale of any product and on the understanding that ChemREADY neither undertakes any obligations or liability for results obtained nor gives any authorization or assurance in the area of patent infringement."